## EMS-SCADA Technical Data
200MW/400MWh BESS — EMS / SCADA TECHNICAL DATA SHEET
OEM to fill YELLOW cells ¦ Energy Management & SCADA System ¦ Ref: CS-0011-171A-G
S.No. | Parameter / Requirement | NTPC RFQ Requirement | OEM Response | Compliance (Y/N/D) | Remarks / Deviation
A. EMS GENERAL
A1 | EMS OEM / Software Developer Name | —
A2 | EMS Software Platform / Version | —
A3 | Total EMS Installations for BESS (MW cumulative) | ≥100 MW
A4 | Largest Single BESS EMS Project (MW) | —
A5 | EMS Architecture (Centralized / Distributed / Cloud-Edge) | — |  |  | On-premise mandatory — Fully local deployment within plant premises; no cloud dependency or external data transfer permitted. Redundant servers (main + hot standby) required per Technical Specification.
A6 | EMS Hardware Platform (Server specs) | — |  |  | Redundant servers required
A7 | Operating System | —
B. EMS FUNCTIONAL REQUIREMENTS
B1 | Real-Time Monitoring of all BESS Parameters | Required – ≤1 sec refresh
B2 | Active Power Dispatch Control | Required – MW setpoint from SLDC/NLDC
B3 | Reactive Power / Voltage Control | Required – kVAr setpoint
B4 | Automatic Generation Control (AGC) Interface | Required per CERC regulations
B5 | Frequency Regulation Mode (Primary/Secondary/Tertiary) | Required – all three
B6 | Peak Shaving / Load Leveling Mode | Required
B7 | Ramp Rate Control | Required – configurable
B8 | SOC Management & Optimization | Required – predictive algorithms
B9 | Degradation-Aware Dispatch | Required
B10 | Scheduling & Forecasting Module | Required – day-ahead, intra-day
B11 | Multi-Unit Coordination (all PCS + containers) | Required
B12 | Black Start Sequence Management | Required if applicable
B13 | Islanding Detection & Management | Required
C. SCADA FUNCTIONS
C1 | SCADA Software Platform | —
C2 | Number of I/O Points Supported | — |  |  | Specify analog + digital
C3 | HMI Screens (Operator Workstation) | Required – min 2 redundant
C4 | Alarm Management System | Required – configurable, multi-level priority
C5 | Event & Sequence of Events (SOE) Recording | Required – ≤1 ms resolution
C6 | Trending & Historical Data Storage | Required – min 5 years
C7 | Report Generation (daily/monthly/annual) | Required – auto & manual
C8 | Web-Based Remote Access | Required – role-based access
C9 | Mobile App / Dashboard | Preferred
D. COMMUNICATION & INTEGRATION
D1 | Protocol to BMS | Modbus TCP/RTU, CAN
D2 | Protocol to PCS | Modbus TCP, IEC 61850
D3 | Protocol to Plant SCADA / DCS | IEC 61850 / DNP3 / Modbus
D4 | Protocol to SLDC / NLDC / RLDC | IEC 60870-5-104 / IEC 61850
D5 | Protocol to Remote Monitoring Center | Required
D6 | Metering Interface (ABT/Special Energy Meters) | Required per CERC
D7 | GPS Time Synchronization (NTP/PTP) | Required – IEEE 1588 PTP preferred
D8 | Redundant Communication Links | Required – dual Ethernet + fiber
D9 | Integration with Plant Weather Station | Required
E. CYBERSECURITY
E1 | IEC 62443 Compliance Level | Required – SL2 minimum
E2 | Role-Based Access Control (RBAC) | Required – multi-tier
E3 | Audit Trail & Logging | Required – tamper-proof
E4 | Encrypted Communication (TLS/SSL) | Required
E5 | Firewall & Network Segmentation | Required
E6 | Intrusion Detection System (IDS) | Required
E7 | Patch Management & Vulnerability Assessment | Required – lifecycle plan
F. EMS HARDWARE & REDUNDANCY
F1 | Server Configuration (Primary + Standby) | Required – hot standby
F2 | Server Specifications (CPU, RAM, Storage) | —
F3 | UPS for EMS/SCADA (kVA, backup duration) | Required – min 2 hours
F4 | Network Switches & Routers | Required – managed, industrial grade
F5 | Fiber Optic Network within BESS Plant | Required
F6 | Operator Workstation Specifications | Required – min 2 nos
F7 | Engineering Workstation | Required – 1 no
F8 | Video Wall / Large Display (if applicable) | —
G. EMS CERTIFICATIONS & TESTING
G1 | Factory Acceptance Test (FAT) Plan | Required – submit with offer
G2 | Site Acceptance Test (SAT) Plan | Required
G3 | IEC 61850 Conformance Certificate | Required
G4 | Cybersecurity Assessment Report | Required
G5 | Software Documentation (SRS, SDD, User Manual) | Required